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APPENDIXD
CROSS-CONNECTION CONTROL PROGRAM

KELSEYVILLE COUNTY WATERWORKS DISTRICT NO. a•
ORDINANCE NO. 1465
An Ordinance Establishing a Cross-Connection Control Program to Protect the Public Water Systems
The Board of Directors of the Kelseyuille County Waterworks District No. 3, Lake County, California, Does Ordain as Follows:

Section 1. Protection of Public Water Systems.
1.1 Purpose and Intent. Pursuant to Section 450 of the Califor-nia Health and Safety Code and Title 17, Section 1174 et seq. of the California Administrative Code, a Cross-connection Control Program is established in the Kelseyville County Waterworks District No. 3 for the following purposes:
(a) To protect the public water supply against actual or poten-tial cross-connections by isolating within the premises con-tamination or pollution that may occur because of some undiscovered or unauthorized cross-connection on the premises;
(b) To eliminate existing connections between drinking water systems and other sources of water that are not approved as safe and potable for human consumption;
(c) To eliminate cross-<:onnections between drinking water sys-tems and other sources of water or process water used for any purpose whatsoever which jeopardize the safety or the drinking water supply; and
•Editor's note-Ord. No. 1465, §§ 1, 2, adopted April 9, 1985, did not expressly amend the Code. At the discretion of the editor, said ordinance has been included as App. D. Section 3, repealer, and § 4, effective date provisions, are not set out herein.
Cross references-Sewer use ordinance for Kelseyville County Waterworks District No. 3, App. B, Art. II; sewer service charge ordinance for KelseyviHe County Waterworks District No. 3, App. C.
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(d} To prevent the making of cross�onnections in the future.
1.2 Definitions. For the purposes of this Ordinance, the follow-ing- terms shall have the following meanin,gs:
(a) Cros9-connection means any unprotected connection between any part of a water system used or intended to supply water for drinking purposes and any source or system containing water or su�stance that is not or cannot be approved as safe, wholesome, and potable for human consumption.
(b) Approued water supply means any water supply approved by or under the public health supervision of a public health ageQCY of the State of California, or its political subdivisions. In determining what constitutes an approved water supply, the State Department of Public Health reserves final judgment as to its safety and potability.
(c) Auxiliary supply means any water supply on or available to the premises other than a public water supply.
(d) Approved check value means a check valve that seats read-ily and completely and has been approved for use in the Kelseyville County Waterworks District No. 3.
(e) Approved double check value assembly nieans an assembly of at least two independently acting approved check valves in-cluding tightly closing shut-off valves on E:'ach side of the check valve assemJ>Jy and suitable leak-detector drains plus connec-tions available for testing the water tightness of each check valve:
(f) Air-gap separation. means a physical break between a sup-
..		ply pipe and a receiving vessel. The air-gap shall be at least double the diameter of the supply pipe measured vertically above the t_op rim of the vessel, in no case less than one inch.
(g) Approved reduced pressure principle backflow prevention deuice means a device incorporating two or more check valves and an automatically operating differential relief valve located between the two checks, two shut-off valves, and equipped with necessary appurtenances for testing. The device shall operate to maintain the pressure in the zone between the two check valves less than the pressure on the public water supply side of the device.
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(h) Approved backflow device means:
(1) An approved double check valve assembly; or
(2) An approved air-gap separation; or
(3) An approved reduced pressure principle backflow preven-tion device.
(i) District water system means a system of wate1· delivery op-erated and maintained by the Kelseyville County Waterworks District No. 3 formed pursuant to Section 55000 et seq. of the Water Code of the State of California.
(j) Premise or premises means land and everything appurte-nant thereto, including but not limited to, buildings, structures, and mobilehomes.
(k) County Utilities Manager means the County Utilities Man-ager for the County of Lake, State of California.
1.3 Cross-connection and Protection Requirements.
3.1 Except as otherwise provided by thjs Ordinance, no person or entity shall cause a connection to be made between plumbing pipes, plumbing fixtures or appurtenances thereof served with water supplied by a distl:ict water system and plumbing pipes, plumbing fixtures or appurtenances thereof served by any other source of water.
3.2 Except as otherwise provided by this Ordinance, no person or entity shall install or use any plumbing pipes, plumbing fixtures or appurtenances thereof which by their construc-tion or means of hook-up, may perm.it a backflow of water or any other liquid or substance into a district water sys-tem or into the service system of a consumer of water from such system.
1.4 Permit Required for Cros�connection.
4.1 Any person or entity that installs or maintains a cross-connection on any premises shall obtain a permit for such cross-connection from the County Utilities Manager.
4.2 As a condition for the issuance of such permit, the person or entity wishing to maintain a cross-connection shall in-stall an approved backflow prevention device.
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4.3 Installation of an approved backflow prevention device shall be required under the following circumstances:
(a) An approved backflow prevention device shall be in-stalled at each service connection of a district water system where the premises served is a,lso served by an auxiliary water supply not approved by the public health agency having jurisdiction.
(b) An approved backflow prevention device shall be in-stalled at each service connection of a district water system where the premises served has upon it any liquid or substance under pressure which may enter a district water system. Such liquid or substance includes, but is not limited to, waters originating from a district water system which have been contaminated below the health standards established for a district water system.
(c) An approved backflow prevention device shall be in-stalled at each service connection of a district water system where the premises served has upon it a cross-connection; provided however, no backflow prevention device is required pursuant to this subsection where such cross-connection has been modified to prevent any contamination of a district water system and such modification has been approved, in writing, by the County Utilities Manager and has been approved by the State or County Health Department.
1.5 Requirements for Installation of B-ackf[ow Prevention Device.
5.1 When a back:flow prevention device is required to be in-stalled pursuant to this Ordinance, the following shall apply:
(a) Any person or entity that is required to install a back-flow prevention device pursuant to this Ordinance shall first obtain a permit for such installation from the County Utilities Manager.
(b) Any backflow prevention device installed must be ap-
proved by the Foundation for Cross-con1?-ection Con-trol and Hydraulic Research of the University of South-ern California.
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(c) Any backflow prevention device shall be installed in accordance with the methods of installation prescribed in the "Manual of Cross-connection Control Procedures and Practices" prepared by the California State De-partment of Health Services Sanitary Engineering Sec-tion or as prescribed and approved in writing at his discretion by the County Utilities Manager.
(d) Any person or entity which owns any premises where
a backflow prevention device has been installed shall have such device inspected annually by a Certified Inspector pursuant to the applicable Rules and Regu-lations of the California State Department of Public Health. A written report of the inspection shall be filed by the owner of the premises with the County Utilities Manager on the second Monday of eac an-uary of each year the device remains installed.
(e) The Kelseyville County Waterworks District No. 3
shall not be liable for any costs for the inspection, repair, or maintenance of any backflow prevention device installed pursuant to this Ordinance. All such costs shall be borne by the owner of the premises.
1.6 Installation of Backfiow Prevention Devices for Premises with Existing Cross-connections.
6.1 Upon adoption of this Ordinance, the CountY, Utilities M.fill:." _
,a er �hall conduct a survey of all premises affected by the requirements of th.is Ordinance to determine those prem-ises which have an actual or potential cross-connection.
6.2 The owner of each premises as determined by the County Utilities Manager shall install or cause to be installed an approved back.flow prevention device within one (1) year from the effective date of this Ordinance.
6.3 Upon the determination by the County Utilities Manager that a backflow prevention device is required upon the premises, the County Utilities Manager shall serve notice upon the owner of said premises, as determined from the last assessment roll, by depositing in. the mail, postage prepaid, certified, return receipt requested, a notice that the prem:ise has been determined to be subject to the pro-
Supp. No. 23	1526.153
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visions of the Ordinance and the steps the owner of the premises must take to comply with such provisions.
6.4 After receiving the notice required by subsection 6.3, above, the owner of the premises shall do one of the following:
(a) Obtain a permit pursuant to the provisions of this Ordinance, and install the device following the proce-dures set forth in subsection 5.1, subdivision (c) of this Ordinance. The total cost of such installation shall be borne by the owner of the premises; or
(b) Request the Cowity Utilities Manager to install the device; provided however, the owner of the premises shall be liable only for those costs incurred for pur-chase of the materials used for such installation. Upon installation, the owner of the premises shall be re-sponsible for all costs of inspection, repair, and main-tenance of the backfl.ow prevention device.
1.7 Discontinuance of Service.
7.1 Service of water to any premises served by a district water system may be discontinued for noncompliance with the provisions of this Ordinance. Service shall be restored only upon compliance with the provisions of this Ordinance.
1.8 Right of Entry.
8.1 The County Utilities Manager, or his designee, shalJ in-spect premises for noncompliance with the provisions of this Ordinance. He shall carry proper credentials of his office, upon exhibition of which he shall have the right of entry, during usual business hours, to inspect all premi!les in the performance of his duty. This right of entry shall be a condition of water serrice in order to provide assurance that the continuation of service to the premises will not constitute a menace to the health, safety and welfare of the people throughout a district water system.
1.9 Certification of Tester.
9.1 Each applicant for certification as a tester of backflow prevention devices shall file an approved application with the Environmental Health Division of the County Health
Supp.No.23	1526.154
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Department together with a fee as may be established by the Board of Directors.
9.2 Competency in all phases of backflow prevention device testing and repair must be demonstrated by means of edu-cation or experience, or both in order to o.btain certific�-tion. The following are minimum requirements:
(a) Applicants shall have had at least two (2) years expe-rience in plumbing or pipe fitting or equivalent qualifications;
(b) Applicants shall hold a valid certification from the American Water Works Association, Califolilia-Nevada Section, or satisfactory completion of the course fot the Training and Certification of Testers fo1· Back.flow Prevention Devices offered by the Foundation for Cross-connection Control and Hydraulic Research, Univer-sity of Southern California, or have equivalent train-ing as determin,ed by the County Utilities Manager and the Director of the Lake County Health Depart-ment or his authorized designee; and
(c) Each applicant shall furnish evidence to show that he has available the necessary tools and equipment to properly test such devices. He shall be responsible for the competency and accuracy of all tests and reports prepared by him.
9.3 The certificate issued to any tester is valid for a period of one (1) year from date of issuance. The certific.ate may be 1·evoked, suspended or not l"enewed for unsatisfactory tes.t-ing, unsatisfactory repairs, or filing a report that misrep-resents the condition of the device tested.
Section 2. Scope.
This Ordinance shall apply to the Kelseyville County Water-works District No. 3.
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